## economic evaluation
EVALUATION OF BIOMASS CHP TECHNOLOGIES
|  | heat-only plant |  | Sterling cogen |  | gasification cogen |  | ORC cogen |  | steam cogen
Technical Data
| thermal output: | 1 | MBTU/h | 0.99609 | MBTU/h | 4.0982 | MBTU/h | 26.5625 | MBTU/h | 68.3036 | MBTU/h
|  | 29.8667 | BHP | 29.75 | BHP | 122.4 | BHP | 793.3333 | BHP | 2040 | BHP
|  | 0.29281 | MWth | 0.29167 | MWth | 1.2 | MWth | 7.7778 | MWth | 20 | MWth
| electrical net output: | n/a |  | 0.035 | MW | 1 | MW | 1.4 | MW | 5 | MW
| electrical efficiency: | n/a |  | 12% |  | 25.91% |  | 18% |  | 25%
| firebox input capacity | 1.2649 | GJ/h | 1.6154 | GJ/h | 13.8947 | GJ/h | 55.0667 | GJ/h | 128.5714 | GJ/h
Fuel Specifics:
| calorific value: | 18.6 | GJ/BDT* | 18.6 | GJ/BDT* | 18.6 | GJ/BDT* | 18.6 | GJ/BDT* | 18.6 | GJ/BDT*
|  | 12.1876 | GJ/tonne (wet) | 12.1876 | GJ/tonne (wet) | 12.1876 | GJ/tonne (wet) | 12.1876 | GJ/tonne (wet) | 12.1876 | GJ/tonne (wet)
| moisture content fuel | 30% |  | 30% |  | 30% |  | 30% |  | 30%
| fuel consumption: | 0.072653 | BDT*/h | 0.092781 | BDT*/h | 0.79805 | BDT*/h | 3.1628 | BDT*/h | 7.3846 | BDT*/h
|  | 0.10379 | t/h (wet) | 0.13254 | t/h (wet) | 1.1401 | t/h (wet) | 4.5183 | t/h (wet) | 10.5494 | t/h (wet)
|  | 230 | lb/h (wet) | 290 | lb/h (wet) | 2500 | lb/h (wet) | 10000 | lb/h (wet) | 23300 | lb/h (wet)
| annual consumption | 310 | t/yr. (wet) | 1060 | t/yr. (wet) | 9100 | t/yr. (wet) | 33900 | t/yr. (wet) | 79100 | t/yr. (wet)
|  | 220 | BDT*/yr. | 740 | BDT*/yr. | 6400 | BDT*/yr. | 23700 | BDT*/yr. | 55400 | BDT*/yr.
|  | 4100 | GJfuel/yr. | 13800 | GJfuel/yr. | 119000 | GJfuel/yr. | 441000 | GJfuel/yr. | 1030000 | GJfuel/yr.
|  |  |  | 49300 | GJfuel/GWhel | 16500 | GJfuel/GWhel | 45200 | GJfuel/GWhel | 28000 | GJfuel/GWhel
| wood fuel costs: | 45 | $/BDT* | 45 | $/BDT* | 45 | $/BDT* | 45 | $/BDT* | 45 | $/BDT*
|  | 31.5 | $/t (wet) | 31.5 | $/t (wet) | 31.5 | $/t (wet) | 31.5 | $/t (wet) | 31.5 | $/t (wet)
|  | 2.4194 | $/GJ | 2.4194 | $/GJ | 2.4194 | $/GJ | 2.4194 | $/GJ | 2.4194 | $/GJ
|  | 8.7097 | $/MWhth | 8.7097 | $/MWhth | 8.7097 | $/MWhth | 8.7097 | $/MWhth | 8.7097 | $/MWhth
Heat Production:
| annual full operating hours²: | 3000 | h/yr. | 8000 | h/yr. | 8000 | h/yr. | 7500 | h/yr. | 7500 | h/yr.
|  | 125 | days/yr. | 333.3333 | days/yr. | 333.3333 | days/yr. | 312.5 | days/yr. | 312.5 | days/yr.
| annual heat production: | 3200 | GJ/yr. | 8000 | GJ/yr. | 35000 | GJ/yr. | 210000 | GJ/yr. | 540000 | GJ/yr. |  | 85952.1891
|  | 900 | MWh/yr. | 2000 | MWh/yr. | 10000 | MWh/yr. | 58000 | MWh/yr. | 150000 | MWh/yr. | 743.2
|  | 3000 | MBTU/yr. | 8000 | MBTU/yr. | 33000 | MBTU/yr. | 199000 | MBTU/yr. | 512000 | MBTU/yr.
| thereof usable heat: | 3200 | GJ/yr. | 8000 | GJ/yr. | 35000 | GJ/yr. | 210000 | GJ/yr. | 540000 | GJ/yr.
|  | 900 | MWh/yr. | 2000 | MWh/yr. | 10000 | MWh/yr. | 58000 | MWh/yr. | 150000 | MWh/yr.
|  | 3000 | MBTU/yr. | 8000 | MBTU/yr. | 33000 | MBTU/yr. | 199000 | MBTU/yr. | 512000 | MBTU/yr.
| thereof heat that can be sold: | 3200 | GJ/yr. | 3200 | GJ/yr. | 35000 | GJ/yr. | 50000 | GJ/yr. | 50000 | GJ/yr.
|  | 100% |  | 40% |  | 100% |  | 23.81% |  | 9.259%
| heat sale price: | 8 | $/GJ | 0 | $/GJ | 8 | $/GJ | 2.4 | $/GJ | 2.4 | $/GJ
|  | 28.8 | $/MWh | 0 | $/MWh | 28.8 | $/MWh | 8.64 | $/MWh | 8.64 | $/MWh
| natural gas price: | 0.29784 | $/m³ | 0 | $/m³ | 0 | $/m³ | 0.29784 | $/m³ | 0.29784 | $/m³
Electricity Production:
| annual electricity production: | n/a |  | 280 | MWh/yr | 7200 | MWh/yr | 9750 | MWh/yr | 36750 | MWh/yr
| net electricity sale price: | n/a |  | 12.5 | Cent/kWh | 9 | Cent/kWh | 21 | Cent/kWh | 12.5 | Cent/kWh
|  |  |  | 125 | $/MWh | 90 | $/MWh | 210 | $/MWh | 125 | $/MWh
Capital Costs:
| initial capital expense (turnkey): | -3500000 |  | -900000 |  | -14000000 |  | -12000000 |  | -20000000
| assumed depreciation period: | 7 | years | 7 | years | 7 | years | 7 | years | 7 | years
| depriciating/interest rate: | 8% | p.a. | 8% | p.a. | 8% | p.a. | 8% | p.a. | 8% | p.a.
| annuity: | -672253.405 | per yr. | -172865.1613 | per yr. | -2689013.62 | per yr. | -2304868.8171 | per yr. | -3841448.0286 | per yr.
Annual O& M costs:
| staffing costs: | -20000 |  | -30000 |  | -60000 |  | -60000 |  | -500000
| wood fuel costs: | -9808.1079 |  | -33401.0151 |  | -287298.9571 |  | -1067440.7747 |  | -2492295.133 |  | -54.25%
| maintenance costs: | -35000 | 10.9375 | -18000 | 64.2857 | -280000 | 38.8889 | -240000 | 24.6154 | -400000 | 10.8844
| total annual O&M costs: | -64808.1079 |  | -81401.0151 |  | -627298.9571 |  | -1367440.7747 |  | -3392295.133
Annual Revenue/Savings:
| from electricity sale/savings: | 0 |  | 35000 |  | 648000 |  | 2047500 |  | 4593750
| from heat sale: | 25600 |  | 0 |  | 280000 |  | 120000 |  | 120000
| total annual revenue/savings: | 25600 |  | 35000 |  | 928000 |  | 2167500 |  | 4713750
Annual Loss/Profit:
| Gross earnings (excl. capital costs): | -39208.1079 |  | -46401.0151 |  | 300701.0429 |  | 800059.2253 |  | 1321454.867
| Net earnings (incl. capital costs): ³ | -711461.5129 |  | -219266.1764 |  | -2388312.5771 |  | -1504809.5919 |  | -2519993.1615
Economic Performance Indicators:
| Simple payback period: | never | years | -19.3961 | years | 46.5579 | years | 14.9989 | years | 15.1348 | years
| electricity generation costs³: | n/a |  | 908.0935 | $/MWh | 311.4167 | $/MWh | 364.3394 | $/MWh | 193.5712 | $/MWh
|  |  |  | 90.8093 | Cent/kWh | 31.1417 | Cent/kWh | 36.4339 | Cent/kWh | 19.3571 | Cent/kWh
* BDT: bone dry metric tonne
² including 1 day maintenance every month
³ assuming figures mentioned in cell C38 and C39 (7 years depreciation period, 8% interest)
yellow marked figures needs to be verified/checked
| calorific value natural gas: | 0.03723 | GJ/m³
| calorific value heating oil: | 46 | GJ/tonne | 0 | MJ/litre | 0 | MJ/litre | 38.548 | MJ/litre | #REF! | MJ/litre